Draft Preventive Maintenance Schedule for Electrical Installation

Document Number: EMC/PM/2026/01

Residential Complex – 1458 Flats, 7 Towers, Mumbai

Date of Issue: July 2026,

Approval Authority: EMC

Distribution: MC, MEP, Electrical Maintenance Team, Safety Committee

- Objective

To ensure electrical safety, reliability, and energy efficiency through structured preventive maintenance aligned with Indian statutory and international electrotechnical standards.

- Scope

Applies to all electrical installations, panels, riser cables, lift feeders, HVAC system for Family Lounge and MPH, Motors, DG sets, and common-area lighting systems across seven towers and outdoor lighting

⚖️ Statutory & Regulatory Mapping

- CEA Regulations (India)

  - Regulation 30: Mandates periodic inspection and documentation of electrical installations.

  - Safety Standards: Aligns with BIS codes (IS 732 for electrical wiring, IS 3043 for earthing).

  - Audit Requirement: Third-party certification for high-load installations.

- IEC / ISO Baselines

  - IEC 60364: International wiring rules for low-voltage installations.

  - ISO 9001: Quality management framework to ensure preventive maintenance is documented and auditable.

  - IEC 60502: Specifies performance and testing of power cables.

- Strategic Upgrade Path

- Lighting Automation (Lift Lobbies):

  - Segregate the lighting circuits in lift lobbies into Ckt A and Ckt B

    - Circuit A: Use Integrated Lux Level meters to control LED lights for central Lobby LEDs

    - Circuit B: Use Astronomical Time Switches (ATS) in front of the Bank of elevators and at the entrance to stair-well

(Target 40–60% energy savings via BEE/MEDA-empanelled agencies.)

- Asset Registry and Lifecycle Management:

- Create an Asset Registry and provide visual ID for each equipment with date of installation and commissioning. Record Age (20–30 years design life, to be ascertained from OEMs).

- Prioritize criticality mapping (feeders for lifts, generators, HVAC).

  - Use colour-coded symbols for various installation.

  - PNG pipeline is already colour-coded

  - Firefighting installation also-colour coded

  - Junction boxes for EMERGENCY circuits need coding

  - Wiring harnesses need proper schematic near the start and end with proper coding

- Stock standardized spares for quick replacement.

- OEM suppliers, Vendors, AMC

  - A comprehensive list of OEM suppliers, spares being procured from vendors registered with the Society

  - Rating/performance grading needs to be maintained.

  - Regular reviews of Annual Maintenance Contracts for Lifts, motors, DG set, etc.

- Preventive Maintenance Schedule – Residential Complex (Mumbai)

- Weekly / Monthly (Routine Inspections)

  - Visual Checks: Inspect riser shafts, meter rooms, and common area panels for sagging cables, moisture ingress, or insulation wear.

  - Cleanliness: Dust and wipe distribution boards, remove cobwebs, and ensure ventilation grills are clear.

  - Lighting & Emergency Systems: Test lift lobby lighting, stairwell emergency lights, and exit signage.

  - Meter Reading & Logging: Record flat-wise and common area consumption; track anomalies (spikes, zero readings).

- Pre-Monsoon (Critical Seasonal Checks – May/June)

  - Waterproofing: Inspect cable trays, junction boxes, and shafts for sealing against rainwater.

  - Drainage Clearance: Ensure electrical rooms have dry floors, sump pumps operational.

  - Insulation Resistance Test (Spot Checks): Perform megger testing on riser cables and lift feeders.

  - Lightning Protection System: Verify earthing pits, surge arrestors, and continuity of down conductors.

- Quarterly / Semi-Annual (Detailed Testing)

  - Thermal Imaging: Scan main LT panels, lift panels, and high-load feeders for hotspots.

  - Connection Tightening: Torque check on busbars, MCCBs, and terminal lugs.

  - DG Set & Transformer Checks: Oil level, breather silica gel, and cable terminations.

- Annual (Deep Diagnostics)

  - Full Insulation Resistance Testing: All riser cables, lift feeders, and common area wiring.

  - Continuity & Grounding Checks: Verify bonding of metallic parts, earthing pits log.

  - Fire Safety Integration: Test fire alarm panels, smoke detectors, and ensure electrical isolation protocols.

- Record Keeping & Compliance Logbook Template (CEA Regulation 30 compliant):

  - Digital Records: Maintain logs in Excel/CMMS software; mandatory for audits.

  - Metering: Use smart meters for tower-wise consumption; monthly reconciliation.

- Standards & References

- CEA Regulations, 2010 – Mandatory inspection & documentation.

- IS 732 – Electrical wiring code.

- IS 3043 – Earthing standards.

- IEC 60364 – International wiring rules.

- BEE Guidelines – Energy efficiency audits.

- Fire Prevention & Hotspot Monitoring

- Infrared Sensors: Quarterly scans for hotspots.

- Fire Extinguishers: CO₂/ABC type in electrical rooms.

- Smoke Detectors: Annual calibration.

- Emergency Drills: Semi-annual evacuation & isolation drills.

- Documentation & Compliance

- Maintain digital CMMS or Excel log with auto reminders for due tests.

- Archive signed reports from external auditors (thermography, harmonics, IR).

- Submit annual compliance summary to the Electrical Inspectorate per CEA Reg 30.

Annexure: Equipment & Instruments lists and Prescribed Test Values